## Sheet1
Risk Assessment Outcomes
Drinking Water System
Date of Risk Assessment:
Participants:
Risk Ranking Threshold Value for CCP determination: 10
Procedure Reference: Risk Assessment Proceedure
Critical Control Limits: Turb = Filter Effluent Turbidity > 0.30 NTU; PSI = Distribution System Pressure < 20 PSI; Cl2 = Free Chlorine Residual < 0.85 mg/L; EHE = Evidence of Hazardous Event occurrence
Hazardous Event Classification | Hazardous Event | Associated Hazards | [8 empty] | Monitoring Processes | [5 empty] | Available Control Measures | [9 empty] | Critical Control Points rating |  |  |  | CCP's and Response proceedures
|  | Source Water Contamination (Biol) | Source Water Contamination(Chem) | Treated Water Contamination | Potential Loss of Water Supply orProduction | Potential Loss of DistributionSystem Pressure | Loss of Controls or Automation | Ineffective chemically-assistedfiltration | Ineffective primary or secondary disinfection | Ineffective or inability to backwash | Routine Regulatory Sampling | Continuous Monitoring | Operational Checks | Alarm Systems | Visual/Audible Observation | Notification from External Parties | No Immediate Control | Redundancy | Preventative Maintenance | Isolation/Bypass Capability | Automatic Switchover Capability | Automatic Shutdown | Manual Operation or Control | Temporary Storage | Treatment Processes | Spare Equipment/Parts Inventory | Likelihood | Severity | Detectability | Overall Risk Value | Critical Control Point? | Associated CriticalControl Limit | Emergency Response Proceedure Reference
Source Water | Private septic systems and discharge of inadequately treated effluent proximal to intake | X | [8 empty] | X | [5 empty] | X | [7 empty] | X |  | 1 | 2 | 3 | 6 | No | N/A | Raw Water Contamination
| Rail car or highway accident in close proximity to source water, treatment plant |  | X | [11 empty] | X | X | X | [6 empty] | X |  |  | 1 | 4 | 1 | 4 | No | N/A | Raw Water Contamination/Chemical Spill
| Periods of high runoff carrying chemical or biological contaminants | X | X | [7 empty] | X |  |  |  | X |  | X | [7 empty] | X |  | 1 | 2 | 3 | 6 | No | N/A | Raw Water Contamination/Chemical Spill
Intake/ Low Lift Pumping | Collapse or breakage of single raw intake pipe |  |  |  | X | [8 empty] | X | [5 empty] | X |  |  |  | X |  |  | 2 | 3 | 1 | 6 | No | N/A | Water Supply Shortage; Raw Water Transmission Main Break
| Low lift pump failure |  |  |  | X | [6 empty] | X | X | X | X |  |  | X | X |  |  |  | X | X |  |  | 2 | 2 | 1 | 4 | No | N/A | Low Lift Pump System Failure
| Raw water flowmeter failure or malfunction | [6 empty] | X | X |  |  | X | X | X | X |  |  |  | X |  |  |  | X |  |  |  | 2 | 3 | 2 | 12 | Yes | Turb; Cl2 | Failure of Chemical Feed Systems; Treatment Process Upset
| Loss of primary heat source at the low lift pumping station |  |  |  | X | [7 empty] | X | X | [9 empty] | X |  | X | 2 | 2 | 2 | 8 | No | N/A | Water Supply Shortage
Coagulation/ Flocculation/ Sedimentation | Coagulant or coagulant aid interruption | [6 empty] | X |  |  |  |  | X | X | X |  |  | X | X |  | X | X |  |  |  |  | 3 | 2 | 1 | 6 | No | N/A | Failure of Chemical Feed Systems; Treatment Process Upset
| Loss of flash mixer (high speed mixer) | [6 empty] | X |  |  |  | X |  | X | X |  |  | X | [8 empty] | 3 | 2 | 2 | 12 | Yes | Turb | Treatment Process Upset
| Failure of the sludge removal system and subsequent floc carryover to filters | [6 empty] | X | [5 empty] | X | X |  |  | X |  |  |  |  | X |  |  | X | 2 | 2 | 1 | 4 | No | N/A | Treatment Process Upset
Filtration & Related Processes | Filter breakthrough event | [6 empty] | X | X |  |  | X | X | X |  |  |  | X | X |  |  | X |  |  |  |  | 2 | 4 | 2 | 16 | Yes | Turb | Treatment Process Upset
| Backwash system failure (i.e. valves, piping, underdrain, pumps) | [8 empty] | X |  |  |  | X | X |  |  | X | X |  |  | X | X |  |  |  | 2 | 3 | 2 | 12 | Yes | Turb | Manual Operation of Treatment Units
| Filter valve failure (filter effluent valve) | [6 empty] | X |  |  |  | X |  | X | X |  |  | X |  |  |  |  | X |  |  | X | 2 | 2 | 1 | 4 | No | N/A | Treatment Process Upset
| Clogged filter | [6 empty] | X |  |  |  | X |  | X | X |  |  | X | X | [7 empty] | 3 | 2 | 1 | 6 | No | N/A | Treatment Process Upset
| Filter PLC failure |  |  |  | X |  |  | X |  |  |  |  | X | X | X | [7 empty] | X | X |  |  | 2 | 3 | 1 | 6 | No | N/A | Manual Operation of Treatment Units
| GAC transfer pump failure | [25 empty] | 2 | 3 | 1 | 6 | No | N/A | Treatment Process Upset
| Failure of backwash surge tank transfer pumps | [8 empty] | X |  | X |  | X | X |  |  | X | X |  | X |  | X |  |  |  | 1 | 2 | 1 | 2 | No | N/A | Treatment Process Upset
Disinfection | Failure of disinfectant chemical feed system | [7 empty] | X |  |  | X | X | X | X |  |  | X | X |  | X |  | X |  |  |  | 2 | 3 | 2 | 12 | Yes | Cl2 | Failure of Chemical Feed Systems; Low Chlorine Residual
Distribution | High lift pump failure |  |  | X |  | X | [7 empty] | X | X | X |  | X | X |  |  |  | X |  |  |  | 1 | 3 | 1 | 3 | No | N/A | High Lift Pump System Failure
| Major water main break or major fire in the community |  |  | X |  | X | [5 empty] | X |  | X |  | X |  | X |  | X |  |  |  |  | X |  | 3 | 4 | 1 | 12 | Yes | PSI | Low Pressure (Distribution System)
| Distribution system vandalism (i.e. illegally opening hydrants) |  |  |  |  | X | [7 empty] | X | X | X | X | [9 empty] | 1 | 2 | 2 | 4 | No | N/A | Low Pressure (Distribution System)
| Major break in the supply line between the WTP and the distribution system |  |  | X |  | X | [5 empty] | X |  | X | X | X |  |  |  | X | [6 empty] | 2 | 4 | 2 | 16 | Yes | PSI, EHE | Water Main Break; Low Pressure (Distribution System)
| Cross-connection to household or industrial plumbing |  |  | X | [6 empty] | X |  |  |  |  | X | X | [7 empty] | X |  | 3 | 3 | 3 | 27 | Yes | EHE | Adverse Water Quality
Electrical/ Mechanical | Lightning strike in the vicinity of the WTP |  |  |  | X | [7 empty] | X | X |  | X | [6 empty] | X | X |  | X | 3 | 3 | 2 | 18 | Yes | EHE | Treatment Process Upset; Control System Failure
| Power failure |  |  |  |  | X | X | [6 empty] | X | X |  |  | X | X | [7 empty] | 2 | 3 | 1 | 6 | No | N/A | Hydro Power Failure
| Standby power (generator) failure at the WTP |  |  |  |  | X | X | [6 empty] | X | X | X |  |  | X | [7 empty] | 2 | 3 | 1 | 6 | No | N/A | Standby Power Failure
|  |  | Revision Date: | [6 empty] | WQMS Reference: | [6 empty] | Internal Reference:
|  |  | 2013-12-05 | [6 empty] | Element # 8 | [6 empty] | VBWDS-QMS-8
|  |  | 2014-10-01 | [6 empty] | Element # 8 | [6 empty] | Machin VBDWS-QMS-8