## CT
| CT Calculation - Surface Water Plant |  |  |  | DATE OF INCIDENT:
CT = (0.353*I)(12.006+e^(2.46-0.073*temp+0.125*C+0.389*pH)) Equation 3-3
(For temperature < 12.5 oC)
CT = (0.361*I)(-2.261+e^(2.69-0.065*temp+0.111*C+0.361*pH)) Equation 3-4
(For temperature > 12.5 oC)
Where:
I = 3, the number of log inactivation required
Temp = temperature in degrees Celcius
C = residual chlorine concentration in mg/L
pH = the negative log concentration of hydrogen ion
e = 2.7183, the base for the natural logarithm Single Clearwell Calculation
PART 1 - Required CT
| Water temperature (oC) |  | 7.5 |  | Blue Cells - Data to be Entered
| Water pH (units) |  | 7 |  | Pink Cells - Calculated Data
| Free Chlorine at clearwell exit (mg/L) |  | 1.1 |  | Yellow Cells - Calculated data from PDDWO
| Target Giardia Logs (0.5 or 1.0) |  | 0.5
| UNDER 12.5 oC, the basic CT value is |  | 22.9943 | mg/L.min.
| OVER 12.5 oC, the basic CT value is |  | 22.686 | mg/L.min.
CT = C (T10/T) x T
Where:
C = Chlorine residual in mg/L
T = Hydraulic retention time in minutes
T10 = Time for 10% of the water to pass through the process
PART 2 - Actual Plant CT
1 | Treated Flow Rate (L/s) |  | 6
2 | Flow (m3/min) |  | 0.36
|  | Area (m2) | Water Depth (m) | Volume (m3) | Baffling Factor | Minimum Tc
[5 empty] | (T10/T) | (min)
3 | Clearwell/High Lift Wells | 155 | 4.1 | 635.5 | 0.5 | 882.6389
4 | Discharge Line (85 m of 200 mm pipe) |  |  | 2.67 | 1 | 7.4167
[5 empty] | TOTAL CONTACT TIME (T10 IN MINUTES) | 890.0556
|  |  |  | TOTAL CT |  | 979.0611 | mg/L.min.
PART 3 - Conclusion
1. If the actual CT value is GREATER than the required CT value, the plant is providing proper disinfection.
2. If the actual CT value is LESS than the required CT value, the plant is not providing proper disinfection and
the incident must be reported as an Adverse. (Refer to the Adverse Reporting Procedure - Chlorine Residuals)